METHOD STATEMENT FOR THERMAL RESISTIVITY TEST

Document Reference Number: EM-7500-M-6051-RA

Location: YASI S/S to BHYG S/S

Work Scope: Thermal Resistivity Test

Client Contract No: N - 19084

Contractor is responsible to prepare method statement for each work activities with compliance to RFC drawings, standard drawings, project specification, prevailing international standards and other relevant approvals and submit it for consultant/TAQA review and approval.

This method statement guideline is prepared in good faith in line with standard engineering practices, to guide, facilitate contractors and standardize the procedural submissions. However, it does not relieve the Contractor from their contractual obligations.

Any discrepancy between this information and actual site conditions shall be verified for its correctness and suitability, as per applicable TAQA procedures and local authorities. The Contractor shall verify and confirm submissions case to case, as per applicable law and standards.

| DOCUMENT REVIEW & AUTHORISATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Contractor |  | APPROVAL |  |  |  |  |
|  |  | Contractor Project Manager | Sub-Contractor Project Manager | Site Manager | Duty Holder/ HSE Manager | Client/Client Representative |
| Name |  | Mr. R Sasitharan | Yousuf Suleiman |  |  |  |
| Signature /Date |  |  |  |  |  |  |
| 1 | Does this document identify high risk activities? Yes / No If answer is “Yes” then risk assessment for each individual high-risk element of work shall be included. |  |  |  |  |  |
| 2 | Does the work scope include temporary works? Yes / No If answer to above question is “Yes” then a separate risk assessment/method statement shall be submitted for temporary works in addition to the method statement risk assessment for the main works |  |  |  |  |  |

| DISTRIBUTION |  |  |  |  |
| --- | --- | --- | --- | --- |
| ORGANISATION NAME | NAME | POSITION | SIGNATURE | DATE |

Sub-Contractor	EPC Contractor	(OE) PM Consultant appointed by the Client	Client

| REVISION RECORD |  |  |
| --- | --- | --- |
| Revision | Date | Comments / Changes |
| 0 | 12/06/2025 | First issue |
| Field Change Notices |  |  |

## Contents

Contents

Abbreviations Used	3

- Purpose and Scope of Works	4

- Programme and Constraints	5

- Surveys and Engineering Design - Completed before start of work	6

- Specifications & Standards	8

- Permits and Permissions	9

- Specific Legal Compliance	10

- Resources & Competency	11

- Communication	13

- Supervision and Responsibilities	14

- Health Impacts	15

- Quality Control	16

- Environmental Impacts	17

- Methodology and Sequence of Works	19

- Emergency Procedures	25

- Appendices	26

- Risk Assessments	27

- Sign Off Sheet	28

# Abbreviations Used

| Abbreviations Used | Definition |
| --- | --- |
| ILO R164 | Occupational Safety and Heath Recommendation |
| ILO R175 | Safety and Heath in Construction |
| PPE | Personal protective equipment |
| COSHH | Control of Substances Hazardous to Health |

# Purpose and Scope of Works

This Method Statement covers all works associated with the followings:

Perform Thermal Resistivity Test

# Programme and Constraints

The working hours shall be in accordance with the contractual agreements for the project, governments guidelines and restrictions imposed by the local authorities.

| Duration of Works |  |  |  |  |
| --- | --- | --- | --- | --- |
| Anticipated start date: 01 Nov 25 |  | Anticipated finish date: 30 Mar 26 |  | Duration: 5 Months |
| Working Hours |  |  |  |  |
| Weekday | Start time: 6:00 am |  | Finish time: 5:00 pm |  |
| Weekend | Start time: 6:00 am |  | Finish time: 5:00 pm |  |
| Generic Constraints |  |  |  |  |
| Environmental: Spilling of fuel or hydraulic oil on site |  |  |  |  |
| Equipment/Plant/Machinery: Borehole equipment |  |  |  |  |
| Site Specific Constraints |  |  |  |  |
| Environmental: Identify Potential Sources of Waste: Wood, paper. Waste Segregation and Storage: Establish clearly labelled waste collection bins for different types of waste, such as recyclables, hazardous materials, and general waste. Ensure proper storage of hazardous materials in designated areas with appropriate containment measures to prevent spills or leaks. Waste Disposal and Recycling: Identify local regulations and guidelines for the disposal of different types of waste, including hazardous materials. Contract with licensed waste management companies for the proper disposal of hazardous materials and recycling of recyclable materials. Implement procedures for the safe transportation of hazardous materials to disposal facilities. Monitoring and Evaluation: Regularly monitor waste generation and disposal practices to identify areas for improvement. Conduct periodic audits to ensure compliance with waste management procedures and regulations. Dust can be produced in dry condition; as a result dust mask may be required. If required, water spray will be used to suppress dust. |  |  |  |  |
| Equipment/Plant/Machinery: |  |  |  |  |
| Existing Infrastructure: |  |  |  |  |
| Utilities: Before starting excavation, refer the GIS drawings, as built drawings, inspect each trial pit location and identify existing underground utilities using a valid calibrated cable detector and GPR detection methods and maintain a proper record to avoid damaging live utilities. |  |  |  |  |
| Access/Egress etc.: Only operatives with valid third-party training certificates will be allowed on site. The site will have designated walkways/walking routes for pedestrians and roads for vehicles, with a speed limit of 20 km/hr. Parking will be available on site for personnel. The work area will be clearly demarcated to restrict access and mitigate unauthorized entry. |  |  |  |  |

# Surveys and Engineering Design - Completed before start of work

If works are within existing infrastructure, then the contractor shall procure any historical or current as built records of the area from the relevant parties, including third party. The Contractor shall provide necessary data survey support from site in order to identify the risk implication based on actual site conditions such as underground services.

The following factors can influence the selection of construction method and equipment: 	Accessibility to the location

Ground conditions

Existing Infrastructure

Proximity to live equipment

| Surveys | Document Reference |
| --- | --- |
| Topography Survey | In Progress |

| Design Reports/Drawings | Document Reference |
| --- | --- |
| PROPOSED 132kV CABLES BETWEEN BHYG G/S – YAS I S/S | N-19083.1 GG ¦ 7500 ¦ U ¦ 0001 |
| PROPOSED 132kV CABLES BETWEEN BHYG G/S – YAS I S/S Trail Pit | N-19083.1 GE ¦ ADTP ¦ N ¦ 0001 |

Project Approved HSE Plan will be followed – HSE Plan No. ESPEC-HSE-D15

HSE Plan

Main Contractor

QA/QC Plan

# Specifications & Standards

| TAQA Specifications & Standards | Document Reference |
| --- | --- |
| General Requirements - Civil Design Fundamentals | S-TR-GEN-CDF |
| Soil Investigation | S-TR-CIVIL-BUILD |

| Industry Specific Standards | Document Reference |
| --- | --- |
| Drilling and foundation equipment HSE | BS EN 16228 |

| TAQA HSE Standards | Document Reference |
| --- | --- |
| Occupational Health and Safety | ILO R164 |
| Safety and Heath in Construction | ILO R175 |
| Occupational Health, Safety Assessment Specification | ISO 45001 |
| System Safety Rules | HSE-HS-13 |
| Procedure for selection & Provision of PPE | HSP.31 |
| COSHH | HSP.30 |

# Permits and Permissions

| Work Permits |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Permit to Dig: Required |  |  |  | Proximity to Electricity: Required (If our work is near existing electrical cables and substations) |  |  |  |
| Permit to Work (daily permit): |  |  |  | Confined Space Permit: Required (If excavation is deep) |  |  |  |
| Working under/adjacent/over utilities: Required ( if our work is involved near existing utilities) |  |  |  |  |  |  |  |
| Temporary Works Permits |  |  |  |  |  |  |  |
| Permit to Load: |  | Permit to Strike: |  |  |  |  |  |
| Permissions required to carry out the works |  |  |  |  |  |  |  |
| Tick as applicable: | Permit to Work |  | Access |  |  | Transfer |  |
| Others: N/A. |  |  |  |  |  |  |  |

| System Identification | Document Reference |  |
| --- | --- | --- |
| Equipment/Tools |  | Certificate/Reference |
| Thermal conductivity apparatus (thermal needle probe) |  | Will be submitted prior to commencing the activity |
| Soil preparation tools (oven, sieve, balance, etc.) |  | N/A |
| Stopwatch or timer |  | N/A |

| NOC | Authority/Utility |
| --- | --- |
| ADDC-TAQA Distribution | YES |
| ADNOC | YES |
| Dolphin Energy | YES |
| Du Telecom | NO |
| Etihad Rail | YES |
| Etisalat Telecom | No |
| GHQ Military Works and Telecom | No |
| ITC Right-of-Way | YES |
| MCC Monitor and Control | No |
| TWS Sewerage AD | YES |
| Tabreed Cooling | No |

# Specific Legal Compliance

| Activity | Document Reference |
| --- | --- |
| Transport of equipment on site | ILO R164 / ILO R175/HSE-HS-13 |
| Unloading equipment | ILO R164 / ILO R175/HSE-HS-13 |
| Soil investigation various methods | ILO R164 / ILO R175/HSE-HS-13 |

| HSE Activity | Document Reference |
| --- | --- |
| Load handling equipment | ILO R164 / ILO R175/HSE-HS-13 |
| Manual handling | ILO R164 / ILO R175/HSE-HS-13 |

# Resources & Competency

|  | Labour / Trades requirements | Numbers |
| --- | --- | --- |
| 1 | Supervisor /Competent Person | 1 |
| 2 | Engineer | 1 |
| 3 | Plant/Drill Operator | 1 |
| 4 | Skilled/unskilled workers | 6 |
|  | Plant and Equipment |  |
| 1 | Thermal conductivity apparatus (thermal needle probe) | 1 |
| 2 | Soil preparation tools (oven, sieve, balance, etc.) | 1 |
| 3 | Stopwatch or timer | 1 |
|  | Materials |  |
| 1 | N/A |  |
| 2 |  |  |
| 3 |  |  |

| PPE |  |
| --- | --- |
| Mandatory: - Gloves - Hard hat - Safety footwear - High visibility vest/jacket Additional when required: - Safety glasses/goggles - Ear defenders | Specialist: |
| Additional site-specific PPE |  |
| The Contractor is responsible for identifying and providing any additional site-specific PPE that is required to safely complete the works. The list of identified PPE shall be included in the table below |  |

| Mandatory Training & Competency Requirements |  |
| --- | --- |
| Position | Requirements |
| Competent Person | TAQA SSR Competency Assurance Guidance Booklet No.2(SSR Summary for Contractors’ CP) Revision 1 1st January2022 HSEQ Department, TAQA |
| Authorized Person |  |
| HSE Engineer | TAQA Contractor HSE Engineer – Job Description Rev 0 |
| Contractor HSE Manager | TAQA Contractor HSE Manager – Job Description Rev 0 |
| Contractor HSE Officer | TAQA Contractor HSE Officer – Job Description Rev 0 |
| Site Manager / Site Engineer | SSR Competency Assurance Guidance Booklet No.2(SSR Summary for Contractors’ CP) Revision 11stJanuary2022HSEQ Department, TAQA |
| Supervisory Staff / Foreman | Follow TAQA requirements* |
| General Operative | Follow TAQA requirements* |
| Plant Operator | Follow TAQA requirements* |

*Any additional requirements to be added by TAQA as part of contractual agreements

# Communication

| Prior to commencing on works | Requirements |
| --- | --- |
| Sub-Contractor pre-start safety meeting | Always, Records required |
| On-site safety induction | Always, Records required |
| On site - competency checks prior to commencing work / QA systems | Always, Records required |

| Routine communication processes | Requirements |
| --- | --- |
| Work crews briefed on RAMS documentation | Sign off required |
| Applicable Toolbox talks (Safety / Environmental / Quality) | Sign off required |
| Contractor safety / progress meetings | Minutes of meeting |
| Workplace safety committee meetings | Minutes of meeting |
| Emergencies | Requirements |
| Emergency response actions identified and communicated | Records required |
| Accident and incident / Near Miss procedures explained | Records required |
| Task specific communication processes | Requirements |
| Follow instruction at all times from the site manager / supervisor relating to all excavation works. | Throughout duration of the works |
| Key Interfaces | Requirements |
| The Contractor shall identify key interfaces additional to the ones identified below: - TAQA - The Contractor - The Subcontractor (if any) Project meetings shall be held regularly. | Throughout duration of the works, Minutes of meeting |
| Subcontractor relationships and overall communication | Requirements |
| The Contractor shall develop a safety and overall communication plan with all Subcontractors. The details are provided below: A two-way daily communication shall be maintained through daily progress reports, toolbox talks, safety briefings, site visits. Etc. All the HSEQ related issues shall be discussed & communicated through weekly HSEQ review meetings & process issues shall be addressed through progress review meetings. Changes required on the method statement shall be notified immediately for the consideration of HSEQ | Where required |
| Rectification & Amendments | Requirements |
| In case of any damage, discrepancy, or change, the contractor shall bring this to the notice of the Consultant or TAQA Engineer and shall proceed further after getting necessary approval from the client. | Yes, records required |

# Supervision and Responsibilities

As a minimum, the Contractor shall undertake the following roles and responsibilities. Any additional site-specific roles that are identified as part of this method statement shall be listed in the table below, with responsibilities:

| Responsibilities | Supervisory Role |
| --- | --- |
| Responsible for execution of the contract and liaison with the Client | Site Agent / Manager |
| Responsible for supervising all teams and controls labour, plant and materials on site. | Foreman |
| Responsible for carrying out daily and process checks | Competent Person / Manager |
| Responsible for the over-all direction, monitoring, coordination, control and supply of required manpower & equipment etc. of all the construction activities and related to the defined scope of work. | Project Manager |
| Responsible for the overall implementation and monitoring of all the activities involved in defined scope of work. | Construction Manager |
| Responsible for the necessary quality assurance and control, documentation, inspections and tests as per TAQA specifications. | QA/QC Engineer |
| Directly involved in the planning and execution of the activities involved in the defined scope of work. They shall be responsible for the preparation of work plan, Safety Action Plan for work permits, if required, prior to the commencement of any work. | Site Engineer |
| Responsible for the direct execution of works involved in work processes according to the approved method statement and drawings and shall directly control and give instruction to the working personnel. He shall also ensure that works are performed with proper tools/equipment, PPE and good housekeeping around the working area. | Foreman |
| Responsible for reviewing work hazards prior to the start of the work and preparing the Safe Work Plan and work permit, if required, prior to submittal to client that must be implemented and observed during works. He must observe compliance of all safety requirements as per works procedures and HSE plan, during works | Safety Engineer |
| Daily and Process Checks |  |
| Checks to be completed | Required (Y/N) |
| Obtaining NOCs & Permits | Y |
| Obtaining existing utilities information | Y |
| Shop Drawing & Method Statement Approval | Y |
| Valid Certificate for Equipments | Y |
| Physical Conditions of Equipments | Y |

# Health Impacts

| Health Impact | Applicable (y) | Health Impact | Applicable (y) |
| --- | --- | --- | --- |
| Toxicity | N/A | Aspiration hazard/Asthma | N/A |
| Skin Irritation/Dermatitis | N/A |  |  |
| Eye Irritation | N/A |  |  |
| Respiratory issues | N/A |  |  |
| Carcinogenetic | N/A |  |  |
| Reproductive toxicity | N/A |  |  |
| COSHH Impacts |  |  |  |
| Substances or materials |  | COSHH assessment required |  |
| Liquids - (Toxic/Corrosive/Flammable/Explosive/Environment dangerous/Irritant/Slip hazard) |  | Not Applicable |  |
| Gases - (Toxic/Flammable/Explosive/Environment Dangerous/Irritant) |  | Not Applicable |  |
| Dust - (Explosion/Irritant/Allergic Issues) |  | Not Applicable |  |
| Fumes - (Toxic/Irritant/Suffocation/Explosive) |  | Not Applicable |  |
| Vapor - (Toxic/Irritant/Suffocation) |  | Not Applicable |  |

# Quality Control

| Name of Site Manager | Telephone Number |
| --- | --- |
| Mr. Abdul Mohsin | +971 58 962 4466 |
| Name of Competent Person | Telephone Number |
| Mr. Jayateja Podili | +971 55 380 1958 |
| Name of Contract Manager | Telephone Number |
| Mr. R Sasitharan | +971 52 851 0425 |
| Name of Person Monitoring Safety | Telephone Number |
| Mr. Rejomon George | +971 55 725 1052 |
| Name of Client Contact | Telephone Number |
| Name of First Aider | Telephone Number |
| Mr Kalimuthan sathya | +971 52 986 1968 |
| Name of Fire Warden | Telephone Number |
| Mr Kalimuthan sathya | +971 52 986 1968 |
| Additional Roles |  |
| Role | Telephone Number |

Project Inspection & Test Plan to be provided by the Contractor, and to contain (at a minimum) the information displayed in the table below.

| Programmed Works | Inspection/Test Activity | Specification Reference | Document Reference | Personnel | Date of Inspection/Test |
| --- | --- | --- | --- | --- | --- |
| Drawing Approval | Document Review | S-TR-CIVIL-SOIL | TAQA Spec. |  |  |
| Method Statement Approval | Document Review | S-TR-CIVIL-SOIL | TAQA Spec. |  |  |
| Thermal Resistivity Test | Soil Measurement | S-TR-CIVIL-SOIL | TAQA Spec. |  |  |
| Sampling | Soil Sample | S-TR-CIVIL-SOIL | TAQA Spec. |  |  |
| Laboratory Testing | Soil, Rock & Water sample | S-TR-CIVIL-SOIL | TAQA Spec. |  |  |
| Report | Geotechnical Report | S-TR-CIVIL-SOIL | TAQA Spec. |  |  |

# Environmental Impacts

The following sections shall be completed in detail by the Contractor. They shall provide relevant references and descriptions. Where necessary/required, additional documents shall be provided as an appendix.

As a minimum the following documents shall be referred by the Contractor. Any additional documents that are applicable shall be added to the table below

| H&S References |  |
| --- | --- |
| ILO R130-Hygiene recommendation |  |
| ILO R175-Safety and Health in Construction |  |
| HSE-HS-13-Safety Rules (TAQA) |  |
| COSHH HSP.30 |  |
| Site Access Notes and Special Arrangements: |  |
| Full time Coaster bus available at site with Air Conditioning in ON position Mobile Toilet Individual water bottles 20 liters cool water Thermos Fire extinguisher |  |
| Site Storage Facilities |  |
| General Storage Requirements All materials, equipment, and plant must be stored securely to prevent theft and damage. Use covered or enclosed storage areas to protect materials from adverse weather conditions. Hazardous Materials Store hazardous materials in designated areas with appropriate containment measures to prevent spills or leaks. Clearly label all hazardous materials and their storage areas. Keep SDS for all hazardous materials on-site and accessible to all relevant personnel. Waste Management Establish clearly labelled waste collection bins for different types of waste (e.g., recyclables, hazardous materials, general waste). Ensure proper storage of waste materials to prevent contamination and environmental hazards. Equipment and Tools Storage Use lockable containers or storage units for small tools and equipment to prevent theft. |  |
| Waste Removal Arrangements |  |
| Waste Skip shall be provided as per Tadweer requirements. |  |

Security Arrangements

- Security guards will be deployed to ensure 24/7 site security, controlling access, and preventing theft, vandalism, and unauthorized entry. - A properly secured, monitored storage facility will be provided on site for hand tools, equipment etc.

Management of Change at Site

Management of change procedure by TAQA – Note for TAQA: To be developed by TAQA if not available. Note: Changes can have an impact on HSE at work. These may include temporary works or works omitted from the original method statement. The control measures for the management of change should include risk assessment, effective coordination and cooperation between all parties involved. These changes should be recoded and signed by all parts involved.

Special Emergency Procedures

Emergency Medical/First Aid response Access and Egress plans Environmental damage Injuries to the employees and general public

Environmental Impact

Spill control – with spill kits available on site. (Diesel, petrol or hydraulic oil) Appropriate fuel storage Appropriate fire prevention

# Methodology and Sequence of Works

#### Employers Requirements

#### Pre-Requisite

Availability of approved location drawings and Ground Investigation Specifications.

All the procedures as defined on the Quality Inspection Plan & Checklist shall be followed. 	Prior to the commencement of the main work, necessary & relevant clearances / RFI /

Approvals shall be obtained from Consultant/TAQA and other concerned authorities.

Verify site condition

Check all environmental constraints and public constraints

Check the accessibility to the site and choose the prefer method of boring 	Ensure the equipment certification is available and within validity period

Check equipment and tools required for the works. Ensure that all equipment’ certificates are available and within the validity period (inspection and maintenance records)

All available options for construction techniques and equipment with respect to the specific site conditions are reviewed and evaluated.

Site personnel are identified fulfilling TAQA competency requirements 	Where necessary, security and Welfare provision are established

The working areas and sites boundaries are clearly up defined and secured

#### Construction & Installation

Security and Welfare provision are established

The working areas and sites boundaries are clearly up defined and secured

Transport of the equipment at site

Underground service detection to ensure there are no services at the borehole location Perform Thermal Resistivity test

Boring & Sampling-in situ

Laboratory investigation on the collected samples Installing Ground water monitoring

Backfilling Reinstatement

Sequence of Work

- Prior Activities - Sequence OF works - Report

Method Statement

This methodology prepared as per the TAQA specification S-TR-CIVIL-SOIL a. Prior Activities - Obtain required permits / NOC from the concerned authorities & As Built drawings showing all existing services for making trial pits - Orientation for all staff regarding safety and environmental requirements before sending to site - All personnel protective equipment must be available. - Obtaining approval from utility authority and relevant department’s prior commencement of work. - No equipment movement or to start work under/close to any adjacent existing OHL or live equipment will be initiated without obtaining all necessary NOCs from the concerned authorities. - Obtaining existing utilities information and excavate trial pits to locate and confirm the existing services at trench route as necessary. - Using suitable approved and calibrated cable avoidance tools (CAT) before boring construction, any possibility of live cables below/ adjacent location will be checked Obtaining the approval of shop drawing ,route approval and method statement prior to start activity - A copy of all the approval shall be available on site all time. - Before working close to live underground or overhead line, LAP and competent personnel approval shall be obtained from TAQA or relevant authorities - All related shop drawings approved - Check for existing utilities before excavation. - Trial pits and service drawings will be verified prior to starting any drilling works. - Check calibration of surveying instruments. All equipment calibration certificates will be available at site for inspection prior to commencement of work. - All related shop drawings approved - Site works will be supervised by qualified Engineers and technician - Application locations will be as per approved construction NOC

b. Sequence Of Works Test Locations For on site testing, the location for the testing shall be identified by the consultant / contractor and agreed by all the interested parties in the project prior to the start of the work. For laboratory testing, collect a representative soil sample from the test identified by the consultant / contractor and agreed by all the interested parties in the project prior to the start of the work. Procedure - Air-dry/oven dry the sample if it is overly wet. - Determine the MDD/OMC value of the sample prior to testing. ( Or direct sample as per instruction from client or contractor) - Assemble the thermal conductivity apparatus according to the manufacturer's instructions. - Insert the calibrated thermal needle probe into the soil. - Ensure that the soil is properly compacted around the thermal probe to eliminate air gaps. - Start the data acquisition system. - Allow the system to reach thermal equilibrium. - Record temperature readings at regular intervals until a stable temperature gradient is achieved. - Measure and record the reading. - Calculate the thermal conductivity/Resistivity of the soil sample. Reporting A comprehensive test report identifying the location and areas of the test conducted and the results obtained along with all the mandatory information as per the standard test method and ISO/IEC 17025:17 shall be submitted. No attempt shall be made in any sort to recommend any further actions, if required. The results submitted shall be used by the consultant or other interested parties as a guideline for planning necessary actions if any required.

.

Location of boreholes, depth and sample types/numbers to be verified by TAQA or their appointed consultant

Verification/Validation pause points

Not Applicable for the activity

Lifting plan arrangement

| Testing and Commissioning – Not Applicable – No HV/LV Equipment |  |
| --- | --- |
| TAQA Approved Personnel | Standard Test Equipment ID No. |

# Emergency Procedures

### The following details shall be completed by the Contractor.

| Hospital (A & E) |  |
| --- | --- |
| NMC Royal Hospital-Khalifa City | 8001122 |
| Burjeel Medical Centre Al Zeina-Al Raha | 025506691 |
| Yas Marina Circuit Medical Centre | 026599800 |
| Emergency Contact Numbers |  |
| Emergency / Police / Fire / Ambulance | Police-999, Fire- 997, Ambulance-998 |
| First Aid Appointed Persons on site | Mr Kalimuthan Sathya |
| First Aid Equipment | First Aid Box |
| Marine Emergencies | 996 |
| In case of damage to any of the services listed below, use the numbers listed to report the damage: |  |
| TAQA | 024164207 |
| Electricity | 991 |
| Water | 992 |

# Appendices

Where required, additional documentation, records, drawings, reports and risk assessments shall be included as appendices by the Contractor.

Document/Drawings/Reports/etc.

# Risk Assessments

- Risk Assessment – 1 - Lifting operation

- Risk Assessment – 2 - Load handling equipment

- Risk Assessment – 3 - Guarding and safety of the borehole location

Risk Assessments

| Prepared by: Site Engineer/Competent Person | Reviewed by: EHS Engineer/ Site Manager | Approved by: Project Manager/Site Manager | Consultant Approval |
| --- | --- | --- | --- |
| Kevin Anto |  |  |  |

# Sign Off Sheet

| Name | Signature | Company | Date |
| --- | --- | --- | --- |

28